# GUIDE SPECIFICATION

# PAC-Shield CI Foil

August 2024

## SECTION 07 21 13 – CO NTINUOUS INSULATION WALL PANELS

** NOTE TO SPECIFIER **

Display hidden notes to specifier by using “Tools”/”Options”/“View”/”Hidden Text”.

Follow the instructions listed in the ** NOTE TO SPECIFIER ** sections included throughout the specification. Edit carefully to suit project requirements. Modify as necessary and delete paragraphs that are not applicable.

This specification is based on the exterior continuous insulation products of Petersen Aluminum Corporation, located at:

1005 Tonne Road

Elk Grove Village, IL 60007 Phone: (800) PAC-CLAD

Fax: (800) 722-7150

E-mail: info@pac-clad.co Internet: www.pac-clad.com

Petersen Aluminum Corporation is the developer and producer of high performance polyisocyanurate insulation panels for the interior or exterior of structural exterior walls of residential and commercial buildings. Petersen’s PAC-Shield products are designed for use in commercial wall applications to provide continuous insulation and weather resistive barrier performance within the building envelope.

This specification includes PAC-Shield CI Foil, an energy efficient rigid insulation panel composed of a closed cell polyisocyanurate foam core bonded online during a restrained-rise manufacturing process to trilaminate foil facers on both sides. PAC-Shield CI Foil can be applied to the interior or exterior of structural exterior walls of residential and commercial buildings and can be used in wall assemblies meeting the acceptance criteria of NPFA 285. For a complete list of NFPA 285 compliant assembly options please call our technical team at 888-746-1114 or reference the report titled Engineering Extensions Based on NFPA 285 Tests on our website, www.pac-clad.com. The impermeable foil facer resists air and water intrusion.

GENERAL

SECTION INCLUDES

PAC-Shield CI Foil Continuous Insulation for Exterior Walls

RELATED SECTIONS

** NOTE TO SPECIFIER ** Delete sections below not relevant to this project; add others as required.

Section 03300 - Cast In Place Concrete: Concrete base wall.

Section 03400 - Pre-Cast Concrete: Pre-cast concrete base wall.

Section 04210 - Clay Masonry: Brick facing.

Section 04800 - Masonry Assemblies: Masonry base wall.

Section 04850 - Stone Facing.

Section 05400 - Cold Formed Metal Framing.

Section 07260 - Vapor Retarders: Vapor retarder materials over insulation to adjacent insulation.

Section 07270 - Air Barriers: Air seal materials over insulation to adjacent insulation.

Section 09110 - Non-Structural Metal Framing.

Section 09200 - Plaster and Gypsum Board.

Section 09220 - Stucco.

REFERENCES

** NOTE TO SPECIFIER ** Delete references from the list below that are not actually required by the text of the edited section; add others as required.

ASTM C 209 – Methods of Testing Insulating Board, Structural and Decorative.

ASTM C 518 – Steady State Thermal Transmission by Means of the Heat Flow Meter Apparatus (R Value)

ASTM C 1289 – Specifications for Faced Rigid Cellular Polyisocyanurate Thermal Insulating Board.

ASTM D 1621 – Test Methods for Compressive Properties of Rigid Cellular Plastics.

ASTM D 2126 - Test Method for Response of Rigid Cellular Plastics to Thermal and Humid Aging.

ASTM D 3273 - Standard Test Method for Resistance to Growth of Mold on the Surface of Interior Coatings in an Environmental Chamber.

ASTM E 84 (UL 723) - Standard Test Method for Surface Burning Characteristics of Building Materials

ASTM E 96 - Test Method for Water Vapor Transmission of Materials.

ASHRAE 90.1-2010 - Energy Standard for Buildings Except Low-Rise Residential Buildings.

IBC Chapter 26 – Foam Plastic Insulation.

Miami-Dade County FL NOA No: 23-1208.13.

CCMC 13460-L; Type 2, Class 1

CAN/ULC S-704 Type 1, Class 1

DrJ Engineering TER 2402-02; 2403-05.

Priest and Associates Engineering Extensions Based on NFPA 285 Tests

NFPA 285 - Standard Fire Test Method For Evaluation Of Fire Propagation Characteristics Of Exterior Non-Load-Bearing Wall Assemblies Containing Combustible Components.

UL 263- Standard for Fire Tests of Building Construction and Materials

**NOTE TO SPECIFIER** System Description section is for PAC-Shield CI Foil wall assemblies that must comply with NPFA 285. This section lists components that may be part of an NFPA 285 compliant assembly. Petersen Aluminum Corporation has an Engineering Extension Report from Priest and Associates that outlines all compliant wall assembly options for Types I, II, III, and IV buildings that can be achieved using PAC-Shield CI Foil. For a complete list of NFPA 285 compliant assembly options please contact our technical team at 800-PAC-CLAD or reference the report titled Engineering Extensions Based on NFPA 285 Tests on our website, www.pac-clad.com. If the assembly does not need to comply with NFPA 285, delete this section.

SPECIFIER INSTRUCTIONS - Continuous insulation wall panels are intended to be used continuous over framing members and to be relatively free of significant thermal bridging. Coordinate with other trades to minimize the penetration of thermal conductors through the wall system. The incorporation of Weather Resistant Barriers (air, vapor and moisture) is a critical element of a continuous insulation wall assembly. It is strongly recommended that the Architect perform a hygrothermal analysis of the assembly at the location of each project using local code requirements and ASHRAE Standards. The calculations should be used to verify the performance of the assembly and to determine the locations of the weather resistant barrier(s) as required.

SYSTEM DESCRIPTION

Exterior Wall Assembly; Exterior Insulation (Table 3 of Engineering Extension Report)

Base Wall

Fire-stopping at floor lines

Cavity Insulation (optional)

Exterior Sheathing or Sheathing/WRB combined product (optional)

WRB on base wall (optional)

Exterior Insulation

WRB on Insulation (optional)

Exterior Cladding System

Exterior Wall Assembly; Interior Insulation (Table 6 of Engineering Extension Report)

Base Wall

Exterior Coating (optional)

WRB over Base Wall Interior (optional)

Continuous Insulation

WRB over Continuous Insulation (optional)

Interior Cladding

** NOTE TO SPECIFIER **- Delete sections below not relevant to this project; add others as required.

DESIGN REQUIREMENTS

Perform work in accordance with all federal, state and local codes.

Physical properties (Foam Core):

Water Absorption: ASTM C 209, less than 0.05 percent by volume.

Compressive Strength: ASTM D 1621; Type I; Grade 2 (20 psi/138 kPa) and Grade 3 (25 psi /172 kPa).

Dimensional Stability: ASTM D 2126, 2 percent linear change (7 days).

Moisture Vapor Permeance: ASTM E 96, less than 0.05 perm (2.875ng/(Pa•s•m2)).

Flame Spread Index: ASTM E 84, less than 75

Smoke Developed: ASTM E 84, less than 450

Resistance to Mold: ASTM D3272 Passed (10)

Service Temperature: Minus 100 degrees F to 250 degrees F (Minus 73 degrees C to 122 degrees C).

3rd Generation Zero ODP Blowing Agent; Contains zero CFCs, HCFCs, or HFC; Virtually zero Global Warming Potential (GWP)

PAC-Shield CI Foil has passed the following:

Meets the current continuous insulation standards of ASHRAE 90.1, IECC and IBC Chapter 26.

NFPA 285 Standard Fire Test Method for Evaluation of Fire Propagation Characteristics of Exterior Wall Assemblies Containing Combustible Components. For a complete list of NFPA 285 compliant assembly options please call our technical team at 888-746-1114 or reference the report titled Engineering Extensions Based On NFPA 285 Test on our website, www.pac-clad.com.

UL 263 Time-Rated Assemblies

PAC-Shield CI Foil is evaluated and listed under DrJ TER 2402-02; 2403-05. Tests include:

Flame spread index of <75 and smoke developed index of <450 when tested in accordance with ASTM E 84.

Classified as Type I in accordance with ASTM C 1289.

SUBMITTALS

Submit under provisions of Section 01300.

Product Data: Manufacturer's data sheets and installation guides on wall panels and fasteners to be used, including:

Preparation instructions and recommendations.

Storage and handling requirements and recommendations.

Installation methods and accessories.

SPECIFIER INSTRUCTIONS - Delete the following paragraphs if LEED is not applicable.

LEED Submittals: Provide documentation of how the requirements of Credit will be met:

List of proposed materials with recycled content. Indicate post-consumer recycled content and pre-consumer recycled content for each product having recycled content.

Manufacturer-Specific Environmental Product Declaration (EPD) which conforms to ISO 14025 and Polyisocyanurate Insulation Manufacturers Association EPD

DrJ Engineering TER 2402-02; 2403-05 (state-specific stamped reports available)

Priest and Associates Engineering Extensions Based on NFPA 285 Tests

Manufacturer's Certificate: Certify panels will conform to specified performance requirements.

QUALITY ASSURANCE

Manufacturer Qualifications: Manufacturer shall be a company that regularly manufactures and assembles specified insulation in house with no outside fabrication operations.

Manufacturer shall have multiple manufacturing facilities to ensure consistency of product supply.

Pre-Installation Meeting: Convene minimum one week before commencing this section's Work. Review installation procedures and coordination required with Related Work and include the following:

Participants: Authorized representatives of the Contractor, Architect, Installer, and Manufacturer.

Review wall assemblies for potential interference and conflicts and coordinate layout and support provisions for interfacing work.

Review continuous insulation wall panels installation methods and procedures related to application, including manufacturer’s installation guidelines.

Review firestopping requirements and weather resistive membrane requirements and placement locations.

Review field quality control procedures.

DELIVERY, STORAGE, AND HANDLING

Good construction practice dictates that all insulations should be protected from moisture and direct sunlight during job-site storage. Pallets of PAC-Shield CI Foil are protected by a 2-step packaging process using shrink wrap and a UV resistant polyethylene bag. This moisture resistant package is designed for protection from the elements during flatbed shipment from our factories to the job-site. Outdoor storage for extended periods of time requires waterproof tarpaulins and elevated storage above ground level a minimum of 2”. Additionally, we recommend slitting the bundle packaging vertically down the center of the two short sides to prevent moisture accumulation within the package.

SEQUENCING

Coordinate with the installation of vapor retarders and air seal materials specified in Section 07260 and Section 07270.

Ensure that products of this section are supplied to affected trades in time to prevent interruption of construction progress.

PROJECT CONDITIONS

Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results. Do not install products under environmental conditions outside manufacturer's absolute limits.

PRODUCTS

MANUFACTURERS

Basis of Design: PAC-Shield CI Foil produced by Petersen Aluminum Corporation, 1005 Tonne Road, Elk Grove Village, IL 60007. Phone: (800) PAC-CLAD. Fax: (800) 722-7150. E- mail: info@pac-clad.com.

** NOTE TO SPECIFIER ** - Delete one of the following two paragraphs; coordinate with requirements of Division 1 section on product options and substitutions.

Substitutions: Not permitted.

Requests for substitutions will be considered in accordance with provisions of Section 01600.

BOARD INSULATION

Roof Board Insulation: Provide products that comply with the following:

** NOTE TO SPECIFIER ** Delete all of the following standards that are not required; coordinate with product specifications.

ASTM standards specified.

Factory Mutual (FM) approvals specified.

Underwriters Laboratories Inc. (UL) classifications specified.

Florida Building Code Approval FL# 46439.

Miami Dade County, Florida Product Control No. 23-1208.12.

ICC – ESR-1208.12

PAC-Shield CI Foil complies with ASTM C1289 Type I and ASTM E85 Class B. Boards are energy efficient rigid insulation panels composed of a closed cell polyisocyanurate foam core bonded on-line during a restrained-rise manufacturing process to trilaminate foil facers on both sides.

Foam Core

Grade 2 (20 psi).

Grade 3 (25 psi).

Panel Size:

** NOTE TO SPECIFIER ** Other sizes are available upon special request (for example: 12 inch, 16 inch, or 24 inch widths by 96 inch length). Note that custom size orders are available. Contact the manufacturer for additional information.

4 feet by 8 feet (1220 mm by 2440 mm).

Additional lengths/width available upon request.

Thickness / R Value: ASTM C 518 at 75 degrees F (23.9 degrees C).

** NOTE TO SPECIFIER ** Select one of the following Grade paragraphs and delete those not required.

1.0 inches (25 mm) / R Value 6.5

1.5 inches (38 mm) / R Value 10.0

2.0 inches (51 mm) / R Value 13.3

2.5 inches (64 mm) / R Value 17.0

3.0 inches (76 mm) / R Value 20.3

3.5 inches (89 mm) / R Value 24.0

4.0 inches (100 mm) / R Value 27.0

Provide to the thickness indicated on the Drawings.

JOINT SEALANT, PANEL FASTENERS, AND ADHESIVES

Liquid Joint Sealants:

Xci BarriBond XL

Xci BarriBond

Xci DynaTrol I-XL Hybrid

Foil Grip 1402 Tape: Foil-faced butyl flashing tape

Backing: 2 mils aluminum foil

Width: 2 to 6 inches

Thickness: 17 mils

AlumaGrip 701 Tape: Foil-faced butyl flashing tape

Backing: 2 mils aluminum foil

Width: 2 to 6 inches

Thickness: 30 mils

ECHOtape MT-A7757: Foil-faced acrylic flashing tape.

Width: Nominal 2.0”, 3.0”, and 4.0”

Thickness: 3.35 mils

Construction Grade Adhesives including: Loctite, Chemlink, DAP, BASF

Insulation Adhesive: CAV-GRIP

Approved Fastening Methods:

Screw type with washers (TRUFAST Walls)

Powder or gas-actuated fasteners with washers

Impalement type (stick pins)

Adhesive: any general construction grade adhesive (not recommended for ceiling applications)

EXECUTION

** NOTE TO SPECIFIER ** - See Petersen Aluminum Corporation Installation Guide for recommended fastening and installation methods. Coordinate panel installation requirements with wall covering manufacturer.

EXAMINATION

Do not begin installation until exterior walls have been properly prepared.

Verify that all wall assembly construction has been completed to the point where the insulation may correctly be installed.

Verify that mechanical and electrical services in walls have been installed and tested and, if appropriate, verify that adjacent materials and finishes are dry and ready to receive insulation.

If wall assembly preparation is the responsibility of another installer, notify Architect of unsatisfactory preparation before proceeding.

PREPARATION

Clean surfaces thoroughly prior to installation.

Prepare surfaces using the methods recommended by the manufacturer for achieving the best result for the substrate under the project conditions.

INSTALLATION

Install in accordance with manufacturer's instructions.

Install without gaps or voids. Do not compress insulation.

Trim insulation neatly to fit spaces. Insulate miscellaneous gaps and voids.

Fit insulation tight in spaces and tight to exterior side of mechanical and electrical services within plane of insulation.

Fasten or adhere insulation as recommended by the manufacturer’s Installation Guide.

Insulation must be protected from open flame and stored in accordance with the manufacturer’s instructions.

SPECIFIER INSTRUCTIONS - During the time between installation of continuous wall insulation panels and the application of the finished exterior cladding, it is recommended that a building wrap be applied over the wall insulation. The incorporation of Weather Resistant Barriers (air, vapor and moisture) is also a critical element of the wall assembly. It is recommended that a hygrothermal analysis of the proposed assembly be conducted to determine the type and locations of a proposed Weather Resistant Barriers. Select one of the following three paragraphs and delete those not required.

Install vapor retarders over insulation panels as specified in Section 07260.

Install air barriers over insulation panels as specified in Section 07270.

PAC-Shield wall insulation is not intended to be left exposed for extended periods of time without adequate protection. If extended exposure is anticipated all exposed foam surfaces exposed to daylight should be taped with a compatible waterproof tape.

Install exterior cladding as recommended by the cladding manufacturer and as specified in other sections of this specification.

PROTECTION

Protect installed products until completion of project.

Cover the top and edges of unfinished wall panel work to protect it from the weather and to prevent accumulation of water in the cores of the panels.

Wet panels shall be allowed to completely dry prior to application of vapor barrier and/or cladding.

Repair or replace damaged products before Substantial Completion.

END OF SECTION